## Instructions
Electrical Load Estimator Tools
Introduction + Disclaimer
These two calcultors are intended to be used by building professionals. Both calculators require some degree of familiarity with the energy code. We have included two different calculators to demonstrate compliance with the energy code. The first is a comprehensive load calculator that assists in calculating the Service Load of a dwelling. This load calculator is compliant with 220.82 of the Electrical Code. The second assists in calculating the Maximum Exiting Load per Code Reference 220.87. It is recommended only building professionals familiar with the energy code use the Service Load Calculation sheet.
Instructions - Maximum Existing Load (220.87)
The maximum existing code is the simpler of the service load calculations. It is determined by taking the maximum output of a home over a year and using the value as a proxy for maximum load. To use this calculator please provide the following information: 1) Service Nominal Voltage (V) 2) Service Rated Current (A) 3) Maximum Existing Demand
Instructions - Service Load Calculation (220.82)
This load calculator is more complex. We recommend only professionals familiar with the electrical code use this calculator. Within the sheet, users will see orange colored cells. These cells are included for users to fill in information as applicable. Additionally, there is a dropdown (Yes or No) for users to fill out for appliances and equipment. Please indicate (Yes or No) if the appliance is applicable for your project. Additionally, the sheet also provides pre-set wattage values for various appliances. If your appliance has a different watt value than the one provided in the sheet please fill in the correct value. Within the range Looking at the sheet, users the sheet, you will find a pre-set series of assumptions. These given conditions are used as an example to navigate the sheet. The given example is provided below:
Review the electrical loads in the table below and check all that exist in the home (be sure to include the proposed heat pump and other building electrification technologies that are being installed). Fill in the corresponding wattage for each item checked, and then add up all the checked items to determine total wattage used. Wattage shown are rough estimates: for a more precise analysis use actual values based on nameplate ratings or consult with an electrical professional. Please note that this form is a voluntary compliance alternative, and you may wish to hire a qualified individual or company to perform a thorough evaluation of your electrical service capacity in lieu of this methodology. Use this electrical load calculation worksheet is at the user’s risk and carries no implied guarantee of accuracy. Users of this form are advised to seek professional assistance in determining the electrical capacity of a service panel.
Given:
1) Square Foot Area of Home = 1,700 square feet (sf)
2) 1.5 kW (1,500 watts) dishwasher
3) 10 kW range
4) 15 kW central heating
5) 29-amp, 240-volt air conditioning
6) 4 kW clothes dryer
7) VA = Volt-amperes
Detailed Instruction - Service Load Calculation:
1) Multiply the ft2 by 3 VA/ft2 (cell I7)
2) Add 1,500 VA for each 2-wire, 20-amp small appliance branch circuit plus the laundry circuit (1,500 VA x 3 = 4,500 VA)
3) Add in the appliance loads. Select (Yes) for given appliance in cells (B14:B31). If appliance value is larger than given value found in cells G14:G31 insert in the following cell (H14:H31).
4) Values will generate in I33 and I34.
5) Insert Central Cooling Load and Central Heating Load in cells G39 and G40 respectively. Next, indicate if the central cooling load/central heating load will has a 120 volt or 240 volt circuit. If VA is already known, insert into cell I40 or I41, respectively. In our example, the heating load of 15000 can be inserted manually.
6) Indicate if Supplemental Resistance Heat Strip (Yes or No) in cell I42.
7) Indicate number of space heaters in cell I43.
8) Indicate the number of Electric Space Heater Nameplate Wattage (per unit) in cell I44.
9) Indicate the Thermal Storage Nameplate Rating (if present) in cell I45.
10) Cell I58 will calculate the Total Amps Required for Service Conductors and Panel. In our example it will generate 154 A as the minimum panel capacity.

## Service Load Calculation
CEC 220.82
Key:
User inputs
User input if applicable
Applicable Equipment | Description of Load |  |  | Default Value (measured in Watts) | Nameplate Rating (measured in Watts) | Applicable Rating (measured in Watts) | Units
General Lighting/Power Load
Required | Insert Total sq. footage of building -> | 1700 |  | Multiply square footage by VA/(ft2 )-> | 3 | 5100 | Watts
Required | Insert # of Kitchen Circuits -> | 2 |  | Mutiply # by volt-amps/circuit -> | 1500 | 3000 | Watts
Required | Insert # of Laundry Circuits -> | 1 |  | Mutiply # by volt-amps/circuit -> | 1500 | 1500 | Watts
Subtotal | [5 empty] | 9600 | Watts
Appliances and Equipment Excluding Air Conditioner(s) |  |  |  | Default | Nameplate Rating | Applicable Rating | Units
Instruction below
Dropdown (Yes or No) | Appliance Name |  |  | Default Value (measured in Watts) | Insert if Different than Default Value | Max Default Value or User Inserted Value (measured in Watts) | Units
No | Microwave |  |  | 1400 |  | 0 | Watts
No | Trash Compactor |  |  | 1000 |  | 0 | Watts
Yes | Dishwasher |  |  | 1500 |  | 1500 | Watts
No | Disposal |  |  | 1000 |  | 0 | Watts
No | Electric Wall Oven |  |  | 2000 |  | 0 | Watts
No | Electric/Induction Cooktop |  |  |  |  | 0 | Watts
No | Electric/Induction Range |  |  | 5000 |  | 0 | Watts
Yes | Electric Clothes Dryer |  |  | 4000 |  | 4000 | Watts
Yes | Electric Heat Pump Clothes Dryer |  |  |  |  | 0 | Watts
No | Electric Clothes Washer |  |  | 500 |  | 0 | Watts
No | Electric Tankless Water Heater |  |  | 15000 |  | 0 | Watts
Yes | Electric Water Heater |  |  | 4000 |  | 4000 | Watts
No | Electric Heat Pump Water Heater |  |  | 550 |  | 0 | Watts
No | Electric Vehicle Supply Equipment (EVSE) - Required for new homes |  |  | 7000 |  | 0 | Watts
No | Evaporative Cooler |  |  | 500 |  | 0 | Watts
No | Pool or Spa |  |  | 2000 |  | 0 | Watts
No | Other |  |  | n/a |  | 0 | Watts
No | Other |  |  | n/a |  | 0 | Watts
No | Other |  |  | n/a |  | 0 | Watts
Subtotal (Appliance and Equipment) | [5 empty] | 9500 | Watts
Total (General Lighting/Power Load + Appliance and Equipment) | [5 empty] | 19100 | Watts
General and Appliance Load Subtotal (sum of all previously indicated)
Subtotal (A) = Total Watts - 10,000 VA | [5 empty] | 9100 | Watts
Subtotal (B) = Subtotal (A) x .40 | [5 empty] | 3640 | Watts
General Load = Subtotal (B) + 10,000 VA | [5 empty] | 13640 | Watts
Heating and Air-Conditioning Load (Include the largest of the following)
Central Cooling Load (Amps x Volts) |  | Insert Central Cooling Load Value Here (Amps) if applicable -> | 29 | Central Cooling Load Value * (Select either 120 Volts or 240 Volts here) -> | 240 | 6960 | Watts
Central Heating Load (Amps x Volts) |  | Insert Central Heating Load Value Here (Amps) if applicable -> |  | Central Heating Load Value * (Select either 120 Volts or 240 Volts here) -> |  | 15000 | Watts
Supplemental resistance strip heat (HP only) | [5 empty] | Yes
Number of electric space heaters | [5 empty] | 4
Electric Space Heater Nameplate Wattage (per unit) | [5 empty] | 1500
Thermal Storage Nameplate Rating (if present) | [5 empty] | 0 | VA or W
1. Air conditioning and cooling (100% of nameplate (NP) rating) = | [5 empty] | 6960 | VA or W
2. Heat pump without supplemental heating (100% NP Rating) = | [5 empty] | 0 | VA or W
3. Heat pump with supplemental electric heat (100% NP plus 65%) = | [5 empty] | 9750 | VA or W
4. Electrical space heating, 4 separate units (65% NP Rating) = | [5 empty] | 3900 | VA or W
5. Electrical space heating > 4 separate units (40% NP Rating) = | [5 empty] | 0 | VA or W
6. Electrical thermal storage and other 100% NP Rating = | [5 empty] | 0 | VA or W
Max HVAC Load | [5 empty] | 9750 | VA or W
Total Current Demand (Volt-Amps) = MAX HVAC Load + General Load | [5 empty] | 23390 | VA or W
Total Current Demand Divided by 240 Volts | [5 empty] | 97.4583 | A
40 Amp Back-feed protection for future Photovoltaic System (Solar Panels) | [5 empty] | 40 | A
Total Amps required for Service Conductors and Panel = | [5 empty] | 137.4583 | A
Rating of Existing/Proposed Electrical Service or Subpanel (Amps) = | [6 empty] | A
Panel Upgrade Required? (Yes ¦ No)
Note on G23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TBD
Note on G26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TBD

## Maximum Existing Load
Maximum Existing Calculator
Service Load Calculations [220.87]
Key:
User inputs
Provide Service Nominal Voltage (V) here -> | 4
Provide Service Rated Current (A) here -> | 4
Service Load Capacity = Nominal Voltage x Rated Current here -> | 16
Provide Recorded Maximum Existing Demand here -> | 4
Limit Existing Load = Recorded Maximum Existing Demand x 1.25 -> | 5
Available Load Capacity | 11
Allowable New Continuous Load | 8.8